AMP113 	PWR REACTOR PRESSURE VESSEL INTERNALS (Version 2023)

Programme Description

This programme manages the effects of age-related degradation mechanisms that are applicable to the reactor pressure vessel internals (RPVIs) components of PWRs, including WWERs. These ageing effects include (a) various forms of cracking, including stress corrosion cracking (SCC), which also encompasses primary water stress corrosion cracking (PWSCC), irradiation-assisted stress corrosion cracking (IASCC), or cracking due to fatigue; (b) loss of material induced by wear; (c) loss of fracture toughness due to either thermal ageing or neutron irradiation embrittlement; (d) changes in dimension due to void swelling; and (e) loss of preload due to thermal and irradiation-enhanced stress relaxation, creep and (f) mechanical damage due to general operation.

The programme includes activities for inspecting, detecting, monitoring, mitigating, evaluating, and, if applicable, dispositioning non-conforming RPVIs components at the facility. The programme is a sampling-based condition monitoring programme with periodic examinations and other inspections of highly affected internals locations. These examinations provide reasonable assurance that the effects of age-related degradation mechanisms will be managed during operation.

The programme includes the selection of baseline components identified as precursors of the expected degradation and specifies their inspection methods. Expansion of the inspection to additional components is required in case of degradation detected in the baseline components. Several components are identified for which the existing programmes are adequate.

### Evaluation and Technical Basis

- Scope of the ageing management programme based on understanding ageing:

The scope of the program includes all PWR RPVIs components that are listed in detail in [1]. The scope of the programme does not include welded attachments to the internal surface of the reactor vessel because these components are assigned to the reactor vessel and can be adequately managed in accordance with AMP102. If the programme is based on a generic evaluation of RPVIs, the applicability of this generic evaluation is demonstrated, and plant-specific changes made to the generic programme as necessary. Examples of generic evaluations of PWR RPVIs are provided in [1] 2, 4-13] and example for national requirements for scope and attributes of PWR RPVIs AMP is provided in [14].

- Preventive actions to minimize and control ageing degradation:

This programme relies on PWR water chemistry control to prevent or mitigate ageing effects that can be induced by corrosion mechanisms (e.g. stress corrosion cracking or any of its forms as PWSCC, IASCC), or loss of material induced by general, pitting or crevice corrosion). Reactor coolant water chemistry is monitored and maintained in accordance with AMP103.

This programme may also rely on minimization of neutron irradiation of RPVIs material using fuel management approaches such as low leakage zone configurations or dummy fuel elements [5].

- Detection of ageing effects:

Detection of ageing effects typically occurs before there is a loss of the structure and component intended function(s). The parameters to be monitored or inspected are appropriate to ensure that the structure and component intended function(s) will be adequately maintained for the period of operation under all design conditions.

The programme manages the following ageing effects and degradation mechanisms that are applicable in general to the RPVI components at the facility:

- Cracking induced by SCC including PWSCC, IASCC, or fatigue - For the detection of cracking, the programme monitors for evidence of surface breaking linear discontinuities if a visual inspection technique is used as the non-destruction examination (NDE) methods, or for relevant flaw presentation signals if a volumetric ultrasonic testing (UT) method is used as the NDE method. The degradation mechanisms mentioned above are specific for a baffle to former assembly (e.g. bolts), a control element assembly, a control rod guide tube, core barrel assembly, a core shroud assembly, a core support barrel assembly, core support shield and lower grid assemblies, a lower support structure.

- Loss of material induced by wear - For detection of loss of material, the programme monitors for gross or abnormal surface conditions that may indicate loss of material occurring in the components. The loss of the material could result in mechanical binding between parts of RPVIs, or RPVIs and the RPV. The detection of the material loss could be indicated by changes in vibration condition of RPVIs induced by the flow characterised by its velocity and direction that can be monitored and evaluated. Measurement of reactor internals vibration most often is performed using mechanical sensors mounted on the reactor vessel or other primary system components, or by analysing the noise content of the signals generated by ex-core or in-core neutron flux detection [15-34]. The elements susceptible to wear are a flux thimble tube (ageing of this component is addressed in AMP 122 [35]), control rod guide tubes, baffle to former bolts, internals hold down spring, an upper core plate alignment pin, a core barrel assembly, a core shroud assembly, a core support barrel assembly, core support shield and lower internals assemblies.

- Loss of fracture toughness induced by either thermal ageing or neutron irradiation embrittlement - The programme does not directly monitor loss of fracture toughness induced by thermal ageing or neutron irradiation embrittlement, or by void swelling and irradiation growth; instead, the impact of loss of fracture toughness on component integrity is indirectly managed by using visual or volumetric examination techniques to monitor for cracking in the components and by applying applicable reduced fracture toughness properties in the flaw evaluations if cracking is detected in the components. All RPVI materials are to some degree sensitive to thermal ageing or neutron irradiation embrittlement especially such elements as a core shroud assembly, core barrel and core baffle assemblies, a core support shield, lower internals and lower support structures and a core basket.

- Changes in dimension due to void swelling and irradiation growth, distortion, or deflection - The programme uses physical measurements to monitor for dimensional changes due to void swelling, irradiation growth, distortion, or deflection (an example model is given in [7]). Changes in dimension could have potential negative impact on, e.g. a core basket, a core baffle, a core shroud, a baffle plate and bolts, a guide tube support.

- Loss of preload caused by thermal and irradiation-enhanced stress relaxation or creep - For the detection of loss of preload, the programme monitors for gross surface conditions that may indicate loosening in applicable bolted, fastened, keyed, or pinned connections. For the detection of loss of pre-load the programme can monitor changes in vibration condition of RPVIs.

- Mechanical damage caused during operation (manipulation during outages) - For the detection of mechanical damage, the programme monitors for evidence of surface breaking, impact traces, distortion of geometry if a visual inspection technique is used as the non-destruction examination (NDE) methods.

Standards for examination methods, procedures, and personnel are provided in the programme, with preference to well-established examination methods. These methods include volumetric UT examination methods for detecting flaws in bolting, physical measurements for detecting changes in dimension, and various visual (e.g. VT-1 or with regard to [5], [6] EVT-1, and VT-3 [5], [6]Error! Reference source not found.) examinations for detection of general surface conditions and detection and sizing of surface-breaking discontinuities. Surface examinations, i.e. ET [5], [6]may also be used as an alternative to visual examinations for detection and sizing of surface-breaking discontinuities.

The performance of periodic non-destructive testing [5], [6] and a comparative analysis of its results can make it possible to monitor the state of the base metal and welds of the RPVIs elements during operation.

For IAEA Member States which apply former Soviet, Russian or national procedures, a description of the visual examination is given in corresponding documents [36] and [37].

For IAEA Member States applying national normative documents, the description is given in corresponding standards, e.g. [38].

Cracking caused by SCC, IASCC, and fatigue is monitored/inspected by either visual examination (for internals other than bolting) or by volumetric UT examination. Visual methods can be used if the component/material has been shown, even with reduced fracture toughness, to withstand flaws large enough to see visually and not to undergo unstable brittle fracture. In addition, visual examinations are used to monitor/inspect for loss of material induced by wear and for general ageing conditions, such as gross distortion caused by void swelling and irradiation growth or by gross effects of loss of preload caused by thermal and irradiation-enhanced stress relaxation and creep.

Detection of ageing in the RPVIs can be implemented through inspections that focus on critical locations of the RPVIs [11], e.g. where the development of degradation is most likely to occur and/or the consequences of failure are the highest. Determination, though measurements and calculations, of the neutron flux distribution [5] can provide information to aid in the assessment of critical locations of the RPVIs.

Another approach that can provide means for detection of ageing effects is the measurement and tracking of the vibration condition of the RPVIs on a long-time basis in order to provide sufficient data for trending.

To aid in the identification of void swelling, the baseline geometry presented in the design documentation of the RPVIs can be a starting point for further trending and evaluation (prior the effects of swelling and irradiation creep could take place). In case of lack of the RPVIs dimensions they could be measured prior to the expected development of degradation and considered a starting point for further trending as well.

- Monitoring and analysis of trends for ageing effects:

The methods for monitoring, recording, evaluating, and trending the data that result from the programme´s inspections shall provide for identification of adverse ageing trends such that corrective action can be performed as necessary in a timely manner.

Monitoring and trending the RPVIs operational history, i.e. the sequence of operational transients characterised by pressure and temperature time courses, can enable the periodical fatigue evaluation in critical locations of the RPVIs, as discussed in AMP101.

Damage of RPVIs elements due to cyclic fatigue can occur due to repeated temperature changes during operation. Monitoring the number of loading cycles of the reactor plant allows recording of all changes in operating parameters (pressure and temperature) necessary for the correct assessment of fatigue of critical sections of the RPVIs elements.

The methods for monitoring and trending neutron swelling through combination of measurements and calculations are described in TLAA109.

- Mitigation of ageing effects:

This programme is a condition monitoring programme that will detect the ageing effects of concern such that, should ageing effects be identified, remediation of the condition can be accomplished, as necessary. Water chemistry control during operation and shutdown is important to avoid corrosion problems. Water chemistry control is maintained in accordance with AMP103.

Using a fuel load patterns with a reduced radiation load on the RPVIs will minimize degradation as a result of radiation embrittlement.

- Acceptance criteria:

The programme provides specific acceptance criteria for the examinations. For components addressed by examinations referenced in AMP102, the acceptance criteria in that programme apply. For other components covered by existing programmes, the examination acceptance criteria are described within the existing programme reference document.

The programme contains the following types of examination acceptance criteria:

- Components whose visual examination (and surface examination as an alternative to visual examination) confirms the absence of the relevant conditions shall be considered acceptable for continued service. In addition, there are requirements to record and disposition surface breaking indications that are detected and sized by visual examinations (e.g. VT-1/EVT-1);

- For volumetric examination, the examination acceptance criterion is the capability for reliable detection of acceptable indications in bolting; in addition, there are requirements for assessment of the system-level/ bolted or pinned assemblies that can accomplish its intended function even with unacceptable volumetric (UT) examination indications that exceed specified limits;

- For physical measurements, the examination acceptance criterion for the acceptable tolerances in the measurements shall be specified with justification to ensure the component can accomplish its intended function even with the dimensional changes;

- For monitoring of vibration conditions, the acceptance criteria shall be specified on the basis of changes in vibration conditions or on the basis of general operational experience of other units of the same technical type (with respect to plant specific condition).

- Corrective actions:

Detected conditions that do not satisfy the examination acceptance criteria are required to be dispositioned through the plant corrective action programme, which may require repair, replacement, or analytical evaluation for continued service until the next inspection. The disposition will ensure that design basis functions of the reactor internals components will continue to be fulfilled for all licensing basis loads and events during intended period of operation. Examples of methodologies that can be used to analytically disposition unacceptable conditions include engineering evaluation methods, for example [39], as well as supplementary examinations to further characterize the detected condition, or, alternatively, component repair and replacement procedures.

- Operating experience feedback and feedback of research and development results:

This AMP addresses the industry-wide generic experience. Relevant plant-specific operating experience is considered in the development of the plant AMP to ensure the AMP is adequate for the plant. The plant implements a feedback process to periodically evaluate plant and industry-wide operating experience and research and development (R&D) results, and, as necessary, either modifies the plant AMP or takes additional actions (e.g. develop a new plant-specific AMP) to ensure the continued effectiveness of the ageing management.

Incidents of PWR internals ageing degradation are identified in IAEA-TECDOC-1557 [3] as well as in [4] and [5]. Examples of reports for PWR internals inspection findings are also included in [40] - [42].

Within past and the current Euroatom framework programme (EP) of the European Commission (EC) a number of research projects were and are currently performed, which address ageing degradation of PWR internals. In the project INTERWELD [43], organized within the 5th Euroatom EP (1999-2002), the irradiation effects on microstructure, properties and residual stresses in the heat effected zone of stainless steel (i.e. 304 and 347) welds in core shrouds were investigated. The objective of the project PERFECT [44], organized within the 6th Euroatom FP (2003-2006), and its follow-up project PERFORM60 [45], organized within the 7th Euroatom FP (2009-2013), was the development of the numerical multi-scale models for the prediction of the degradation of reactor pressure vessels and reactor internals under LTO. A 4-year (2015-2019) European research project SOTERIA in the field of nuclear safety concentrated on the ageing phenomena occurring in reactor pressure vessel (RPV) steels and in the internal steels (internals) in order to provide crucial information to regulators and operators to ensure safe long-term operation (LTO) of existing European nuclear power plants (NPPs).

Westinghouse has communicated an operating experience related to clevis insert cap screw (bolt) degradation. The Technical Bulletin [46] provides a summary of the operating experience as well as root cause findings and the applicability of these findings on Westinghouse and Combustion Engineering pressurized water reactor designs. The Technical Bulletin also reviews the safety implications of the operating experience and root cause analysis results as well as inspection recommendations for licensees to consider including as part of their ageing management programme [46].

Operating experience at Salem Unit 1, Beaver Valley Unit 1, and Surry Unit 1 as well as the results of subsequent evaluations related to thermal shield flexure degradation are described in TB 19-5 rev 2 [47]. It is addressed both safety and “physical asset management and preservation” lessons learned from the recent operating experience [47].

- Quality management:

In line with SSG-48 [48], Section 4.9 of the IGALL Safety Report [49] gives general information about the expected contents of this attribute in terms of (a) administrative controls, (b) safety analysis report supplements, (c) performance indicators, (d) confirmation (verification) process and (e) data collection and record keeping. Further guidance is available in Paras 3.13.16 – 3.13.17 of SSG-61 [50] on the safety analysis report supplements, in GS-G-3.1 [51] on the confirmation process (paras 6.76 – 6.77 for preventive actions and paras 6.66 – 6.75 for corrective actions), while Section 2 of SRS No. 106 [52] contains good practices on data collection and record keeping for ageing management.

In addition to that the following specific information is relevant for this AMP. Examples of qualitative performance indicators are as below:

Adequacy of AMP

Definition: If it was necessary to modify the AMP because of operating experience of the plant (i.e. AMP appeared not to be proper nor properly meet its objectives), the indicator is 1, otherwise 0.

Explanation: Either because of the degradation occurrence, progress or becoming unacceptable or for other technical reason (not appropriate ISI, change of maintenance strategy/tools, change of monitoring device or frequency, etc.) the AMP had to be modified and/or revised. If the reason is only formal/regular review or to reflect an administrative change, the indicator should remain zero.

Performance of AMP activities

Definition: If activities scheduled in the AMP are not completed, the indicator is 1, otherwise 0.

Explanation: This indicator detects if any preventive, mitigative, ISI, maintenance, monitoring or corrective action did not take place as scheduled.

Data management

Definition: If the parameters measured, monitored, etc., indicated by the AMPs, are analysed and the analysis does not give useful or convincing information (probably compared with non-conformity reports), the AMP or the AMR must be analyzed. If true, the indicator is 1, otherwise 0.

Explanation: One of the objectives of the monitoring and trending is to find if the AMP applied is appropriate. If the monitoring results do not provide appropriate information and further actions should be taken in order to confirm if the AMP is appropriate, the monitoring activity may need to be modified and this could be detected by the indicator.

Correctness of ageing prediction

Definition: Deviation of predicted and detected aged condition of the component. Ratio of the absolute value of the difference and the predicted value.

Explanation: Comparison of the predicted and measured characteristic parameter of a given degradation mechanism, such as wall thickness, number (or density) of flaws, growth of flaws, embrittlement, hardness. Frequency of evaluation of this indicator needs to be adjusted to the measurement frequency of the parameter (during maintenance, ISI, etc.).

The examples of quantitative performance indicators are as below:

Trends of data relating to RPV internals failure or degradation

Definition: Trend of data relating to RPV internals failure or degradation in material condition involving changes in crack dimensions, in a value of fracture toughness, in loss of material, dimensional changes within the period of time (e.g. 3, 5, 10 years).

Explanation: The indicator shows the health of different RPV internals and if the trend of the several years accelerates, is in steady progress or slows down it allows to evaluate the effectiveness of preventive, mitigating and corrective actions.

### References

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: PWR Internals Material Aging Degradation Mechanism Screening and Threshold Values MRP-175, Rev. 0 (EPRI 1012081) EPRI Palo Alto CA, 2005.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: PWR Internals Material Aging Degradation Mechanism Screening and Threshold Values MRP-175 Rev 1 (EPRI 3002010268), EPRI Palo Alto CA, October 2017.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: PWR Vessel Internals, 2007 Update, IAEA-TECDOC-1557, IAEA, Vienna, June 2007.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: Pressurized Water Reactor Internals Inspection and Evaluation Guidelines MRP-227-A, (EPRI 1022863), EPRI, Palo Alto, CA, December 2011.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: Pressurized Water Reactor Internals Inspection and Evaluation Guidelines MRP-227 Revision 1-A, (EPRI 3002017168), EPRI, Palo Alto, CA, December 2019.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: Inspection Standard for PWR Internals MRP-228, Rev. 4 (EPRI 3002018245), EPRI, Palo Alto, CA, November 2020.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: Improvement of the Cluster Dynamics Model for the Prediction of Void Swelling in Austenitic Stainless Steel MRP-391 (EPRI 3002003083). EPRI, Palo Alto, CA, October 2014.

- THE JAPAN SOCIETY OF MECHANICAL ENGINEERS, JSME S NA1, Code for Nuclear Power Generation Facilities - Rule on Fitness-for-Service for Nuclear Power Plants, JSME.

- JAPAN NUCLEAR ENERGY SAFETY ORGANIZATION, Aging-Related Technology Assessment Review Manual Irradiation-Assisted Stress Corrosion Cracking (IASCC), JNES-SS-0809, JNESO, 2009.

- ROSENERGOATOM, Strength and Residual Lifetime Calculation Methodology for VVER-1000 Internals at Lifetime Extension up to 60 years, RD EO 1.1.2.99.0944-2013, 2013.

- ROSENERGOATOM, Guidance on Strength Calculation of Equipment and Pipelines of Reactor Units RBMK, VVER and EGP during Operation Phase, Including Operation beyond the Design-Basis Lifetime, RD EO 1.2.2.05.0330-2012, 2012.

- M. Svrcek, Evaluation of the VVER 440 Reactor Pressure Internals (Core Basket) Integrity with Respect to the Radiation Swelling, Radiation Creep and Formation of Limit Embrittlement Area, DITI 2301/740, UJV Rez, a.s., 2019.

- V. Pistora, M. Posta, V. Moskalenko, Evaluation of the VVER 1000 Reactor Vessel Internals (Core Shroud) Integrity with Respect to the Radiation Swelling, Radiation Creep and Formation of Limit Embrittlement Area, DITI 2301/878, UJV Rez, a.s., 2019.

- Hungarian Atomic Energy Agency: Guideline 4.12. Ageing Management during the Operation of NPPs, March 2016.

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Current Applications of Vibration Monitoring and Neutron Noise Analysis, NUREG/CR-5479 ORNL/TM-11398, 1990.

- Végh, J. et al, Implementation of New Reactivity Measurement System and New Reactor Noise Analysis Equipment in a VVER-440 Nuclear Power Plant, IEEE Transactions on Nuclear Science, Volume: 57 Issue:5 pp. 2689 - 2696 ISSN: 0018-9499, October 2010.

- Pazsit I., Demaziere C., Theoretical investigation of the MTC noise estimate in 1-D homogeneous systems, Annals of Nuclear Energy, ISSN 0306- 4549, Volume 29, Issue 1, pp. 75 – 100, 01/2002.

- Kiss S., Lipcsei S. and Végh J., Overview of Recent KFKI AEKI Activities in the Field of Plant Surveillance and Diagnostics, Power Plant Surveillance and Diagnostics: Applied Research with Artificial Intelligence, Springer-Verlag Berlin and Heidelberg GmbH & Co. K, pp. 51-62.

- Pázsit, C. Demazière, V. Arzhanov, Research and Development Program in Reactor Diagnostics and Monitoring with Neutron Noise Methods, SKI Report 2003:08, ISSN 1104–1374, January 2003.

- D. Wach and G. Kosály: Investigation of the joint effect of local and global driving sources in incore-neutron noise measurements, Atomkernenergie, Vol. 23., pp. 244-250, 1974.

- Katona T., L., Mesko, G. Por, J. Valko: Some Aspects of the Theory of Neutron Noise, Progress in Nucl. Energy, Vol.9, (1982) 209, 1982.

- Pór Gábor, Kosály György globalis-lokális koncepciojának megjelenése és annak továbbfejlesztése a hőhordozó-forgalom meghatározásában, Nukleon, december II. évf. (2009) 51, 2009.

- R. Kozma, Studies on the Relationship between the Statistics of Void Fraction Fluctuations and Parameters of Two-Phase Flows, Int. J. Multiphase Flow, Vol. 21, No. 2. 241-251, 1995.

- Kozma, R., Noise Investigations on Boiling Effects in a Simulated MTR-Type Fuel Assembly, Delft University Press, ISBN-90-73861-04-7, 1992.

- R. Kozma, H. van Dam, J.E. Hoogenboom, Identification of Flow Patterns by Neutron Noise Analysis During Actual Coolant Boiling in Thin Rectangular Channels, Nucl. Technol., Vol. 100, 97-110, 1992.

- Katona, R. Kozma, Problems of Estimation of the Thermohydraulic Parameters Using Neutron and Temperature Noise Signals, Progress in Nuclear Energy, Vol.21, 431-445, 1988.

- L.J. Kostić, J. Runkel, D. Stegemann, Thermohydraulics surveillance of pressurized water reactors by experimental and theoretical investigations of the low frequency noise field, Progress in Nuclear Energy, Volume 21, Pages 421-430, 1988.

- T.H.J.J. van der Hagen, J. van der Voet, Interpretation of velocities determined by noise analysis for various void fractions and flow regimes in twophase flow, Progress in Nuclear Energy, Volume 21, Pages 565-573, 1988.

- Hampel R, Fleischer S, Dräger F, Maekawa T, Water Level Measurement System For Boiling Water Reactors Using Internal Gamma Radiation – Neural Network Application, Intelligent Techniques And Soft Computing In Nuclear Science And Engineering, pp 504-511.

- R. Kozma, J.E. Hoogenboom, Flow Measurements Using Noise Signals of Axially Displaced Thermocouples, Annals of Nuclear Energy, Vol. 17, No. 9, pp. 493-513, 1990.

- Windberg P, Katona T, Mauersberger H, Rindelhardt U., Teoreticheskoe i eksperimentalnoe issledovanie akusticeskoy peredatochnoy harakteristiki impulsnikh trubok. Budapest: KFKI, 38 p., KFKI; 1979/43, ISBN:963 371 560 1, 1979.

- Katona T, Nagy I, Interpretation of the low-frequency pressure fluctuations in PWR-s. 16th Informal Meeting on Reactor Noise, Budapest, Magyarország, 1983.05.18-1983.05.20, 1983.

- Nagy I, Katona T, Theoretical investigation of the low-frequency pressure fluctuation in PWRs. Progress in Nuclear Energy 15:(1-3) pp. 671-683, 1985.

- Katona T., Statistical analysis of subcooled boiling acoustic noise. Budapest: KFKI, 27 p., KFKI; 1981/14, ISBN:963-371-791-4, 1981.

- INTERNATIONAL ATOMIC ENERGY AGENCY, AMP 122 Ageing Management Programme of PWR Flux Thimble Tube Inspection.

- PNAE G-7-010-89 Equipment and Pipelines in Nuclear Power Installations. Welds and Claddings. Inspection Rules.

- NP-084-15, Federal Norms and Rules in the Field of Atomic Energy Use. Rules for Monitoring the Base Metal, Welded Joints and Deposited Surfaces of Equipment, Pipelines and Other Elements of Nuclear Power Plants.

- Normative Technical Documentation of Association of Mechanical Engineers of Czech Republic for Design and Life Time Assessment of Components and Piping in VVER NPPs During Operation, 2020.

- VERLIFE, Unified Procedure for Lifetime Assessment of Components and Piping in WWER NPPs during Operation, COVERS–WP-D4.10, European Commission, ASME 2009 Pressure Vessels and Piping Conference, Volume 1: Codes and Standards, Prague, Czech Republic, July 26–30, 2009.

- ELECTRIC POWER RESEARCH INSTITUTE letter report MRP 2014-009, dated 5/12/2014 “Biennial Report of Recent MRP-227-A Reactor Internals Inspection Results” (NRC ADAMS no. ML14135A383 through ML14135A385).

- ELECTRIC POWER RESEARCH INSTITUTE letter report MRP 2016-008, dated 5/18/2016 “Biennial Report of MRP-227-A Reactor Internals Inspection Results” (NRC ADAMS no. ML16144A789).

- ELECTRIC POWER RESEARCH INSTITUTE letter report MRP 2018-025, dated 7/25/2018 “2018 Biennial Report of Recent MRP-227-A Reactor Internals Inspection Results” (NRC ADAMS no. ML18204A161).

- EUROPEAN COMMISSION, Irradiation Effects on the Evolution of the Microstructure, Properties and Residual Stresses in the Heat Affected Zone of Stainless Steel Welds (INTERWELD) - Financial Technical Report, Contract No; FIKS-CT-2000-00103, 2006.

- EUROPEAN COMMISSION, Prediction of Irradiation Damage Effects on Reactor Components (PERFECT), Final Activity Report, Contract No. F160-CT-2003-508840, EUR24455, 2008.

- EUROPEAN COMMISSION, Prediction of the Effects of Radiation for Reactor Pressure Vessel and In-Core Components Using Multi-Scale Modelling - 60 years’ Foreseen Plant Lifetime (PERFORM60) Project Final Report, projected ref.232612, 2016.

- WESTINGHOUSE, Technical Bulletin: Reactor Internals Lower Radial Support Clevis Insert Cap Screw Degradation, TB-14-5, Westinghouse, Cranberry Township, PA (2014).  (Available starting on page 10 of NRC ADAMS Accession No. ML14302A072, at https://www.nrc.gov/docs/ML1430/ML14302A072.pdf

- WESTINGHOUSE, Technical Bulletin: Westinghouse NSSS PWR Thermal Shield Degradation, TB-19-5, Rev. 2, Westinghouse, Cranberry Township, PA (2022).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management and Development of a Programme for Long Term Operation of Nuclear Power Plants, Specific Safety Guide, Safety Standards Series No. SSG-48, IAEA, Vienna (2018).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management for Nuclear Power Plants: International Generic Ageing Lessons Learned (IGALL), Safety Reports Series No. 82 (Rev. 2), IAEA, Vienna. Preprint.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Format and Content of the Safety Analysis Report for Nuclear Power Plants, SSG-61, IAEA, Vienna (2021).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Application of the Management System for Facilities and Activities, GS-G-3.1, IAEA, Vienna (2006).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management and Long Term Operation of Nuclear Power Plants: Data Management, Scope Setting, Plant Programs and Documentation, Safety Report Series No. 106, IAEA, Vienna (2022)