## AMP 120 	SELECTIVE LEACHING (VERSION 2023)

Programme Description

The programme for selective leaching (dealloying) of materials ensures the integrity of the components made of gray cast iron, ductile iron, and copper alloys (except for inhibited brass) that contain greater than 15 percent zinc or 8 percent aluminum exposed to a raw water, closed-cycle cooling water (CCCW), treated water, waste water, soil, or groundwater environment. Depending on the environment, the AMP includes one-time, opportunistic, and/or periodic inspections of selected components that are susceptible to selective leaching. Inspection techniques utilized determine whether loss of material due to selective leaching is occurring and whether selective leaching will affect the ability of the components to perform their intended function for the intended period of operation.

Susceptible materials, high temperatures, stagnant-flow conditions, and a corrosive environment, such as acidic solutions for brasses with high zinc content and dissolved oxygen, are conducive to selective leaching [1-2, 10, 14]. The selective leaching process involves the preferential removal of one of the alloying components from the material. Dezincification (loss of zinc from brass) and graphitic corrosion (removal of iron from gray cast iron and ductile iron) are examples of such a process. A de-alloyed component often retains its shape and may visually appear to be unaffected; however, the functional cross-section of the material has been reduced. The ageing effect attributed to selective leaching is loss of material because the affected volume has a permanent change in density and does not retain mechanical properties that can be credited for structural integrity.

### Evaluation and Technical Basis

- Scope of the ageing management programme based on understanding ageing:

The programme for selective leaching (dealloying) of materials ensures the integrity of the components made of gray cast iron, ductile iron, and copper alloys (except for inhibited brass) that contain greater than 15 percent zinc or 8 percent aluminum exposed to a raw water, closed-cycle cooling water (CCCW), treated water, waste water, soil, or groundwater environment. Components include piping, valve bodies and bonnets, pump casings, and heat exchanger components.

- Preventive actions to minimize and control ageing degradation:

Although the programme does not provide guidance on preventive actions, it is noted that monitoring of water chemistry to control pH and concentration of corrosive contaminants and treatment to minimize dissolved oxygen in water are effective in reducing selective leaching. Water chemistry is managed by the AMP 103. Use of cathodic protection and coatings can be effective means of reducing or minimizing the occurrence of selective leaching degradation.

- Detection of ageing effects:

Inspections and examinations may consist of the following methods. The detection methods below are listed in order of increasing complexity of deployment and detection capabilities. If a given inspection method yields inconclusive or potentially unacceptable results, a more capable method may be chosen for follow-up inspection and disposition of results.

For gray cast iron and ductile iron:

- Visual inspections of accessible surfaces for evidence of non-uniform texture, discolorations, and or the presence of tubercules, corrosion, scale, and deposits on the internal surfaces.

- Graphitic corrosion of cast irons cannot be reliably detected through only visual means. Therefore, visual inspections are supplemented by mechanical examination techniques, particularly in the areas of interest determined by visual inspection. Mechanical examination techniques may include actions such as chipping, scraping, scratching, or otherwise abrading exposed and accessible surfaces.

- Brinell hardness testing (where feasible, based on form and configuration of the component) or other industry-accepted mechanical inspection techniques can be used on the affected surfaces of components to determine if selective leaching has occurred, but is not accurate for determining the extent of selective leaching [13].

- Nondestructive examination techniques demonstrated to be capable of detecting the presence and/or extent of selective leaching on the component. Technical justification demonstrating the effectiveness of the non-destructive examination process shall be included as part of the programme’s documentation. [10-12, 15-17], where [15-17] are results of recent R&D.

- Destructive examinations may be used to confirm the presence and depth of possible de-alloying.

For copper-based alloys:

- Visual inspections of accessible surfaces. Selective leaching generally does not cause changes in dimensions and is difficult to detect by visual inspection. However, selective leaching may be more readily identified through a change in color, such as from a normal yellow color to a reddish copper color or green copper oxide. For copper alloys with >15% zinc, a white/gray meringue deposit may develop on the surface. [10, 14]

- Brinell Hardness testing (where feasible, based on form and configuration) or other industry-accepted mechanical inspection techniques can be used on the affected surfaces of the selected set of components to determine if selective leaching has occurred, but is not accurate for determining the extent of selective leaching [10, 13].

- Nondestructive examination techniques demonstrated to be capable of detecting the presence and/or extent of selective leaching on the component. Technical justification demonstrating the effectiveness of the non-destructive examination process shall be maintained in an auditable and retrievable format. [10-12]

- Destructive examinations may be used to confirm the presence and depth of possible de-alloying.

Inspections, where possible, focus on the bounding components, or those considered the most susceptible to ageing, based on time-in-service and severity of operating conditions for each population. One-time and periodic inspections are conducted of a representative sample of each population. A population is defined as the same material and environment combination.

One-time inspections are only conducted for components exposed to CCCW or treated water when no plant-specific OE of selective leaching exists in these environments.

Opportunistic and periodic inspections are conducted for components exposed to raw water, waste water, soil, or groundwater and for components in CCCW or treated water where plant-specific OE includes selective leaching in these environments. Whenever components are opened, or buried or submerged surfaces are exposed, opportunistic inspections are conducted when allowed by plant and operating conditions. Periodic inspections are conducted according to the plant specific evaluations and national regulatory requirements.

Because selective leaching is a slow acting corrosion process, initial inspections are to be performed within 5 years prior to entering the period of long term operation. Follow-up of unacceptable inspection findings includes an evaluation using the corrective action programme and a possible expansion of the inspection sample size and location.

Where practical, the inspection includes a representative sample of the system and focuses on the bounding components, or those considered the most susceptible to selective leaching due to time-in-service, severity of operating conditions, and lowest design margin [3]. Twenty percent of the population with a maximum sample of 25 constitutes a representative sample size. Otherwise, a technical justification of the methodology and sample size used for selecting components for the one-time inspection is included as part of the programme’s documentation [18]. Each group of components with different material/environment combinations is considered a separate population. For subsequent inspections following this one-time inspection or initial inspections, a reduction in sampling may be technically justified as discussed in [4]. Reduced sampling guidance for components is further described in [5].

- Monitoring and analysis of trends for ageing effects:

Where practical, results of periodic inspections are trended in order to project observed degradation to the end of intended period of operation or the next scheduled inspection, whichever is shorter. Corrective actions are taken when trending results project that a loss of intended function could occur prior to the next inspection.

- Mitigation of ageing effects:

This programme is a condition monitoring programme and does not mitigate selective leaching effects. However, since selective leaching is dependent on environmental conditions and presence of a susceptible material, mitigative actions can be made regarding the environment (decrease of the oxygen level and increase of the pH) and the materials (selection of non-susceptible materials in the design phase or upon replacement). Use of cathodic protection and coatings can be effective means of reducing or minimizing the occurrence of selective leaching degradation.

- Acceptance criteria:

The acceptance criteria are:

| Acceptance Criteria | Gray Cast Iron / Ductile Iron | Copper Alloy and Al Bronze |
| --- | --- | --- |
| Visual Inspection | The presence of no more than a superficial layer of dealloying, as determined by removal of the de-alloyed material by chipping or scraping Note 1. | No noticeable change in color from the normal yellow color to the reddish copper color or green copper oxide If green oxide is identified, it should be removed, and the base metal should be inspected for a change in color from the normal yellow color to the reddish copper color. For copper alloys with >15% zinc, a white/gray meringue deposit may develop on the surface under certain environmental conditions. |
| Mechanical Examination |  | N/A |
| Hardness Testing | No more than a 20 percent decrease in hardness | No more than a 20 percent decrease in hardness |
| Demonstrated NDE Techniques | Surface Techniques: no evidence of selective leaching beyond a superficial layer. Volumetric Techniques – see Note 2 | Surface Techniques: no evidence of selective leaching beyond a superficial layer. Volumetric Techniques – see Note 2 |
| Destructive Examinations | See Note 2. | See Note 2. |

Table 1. Acceptance Criteria

Note 1 Mechanical examinations should be used to augment visual examinations

Note 2: The remaining wall thickness of the component, in the region of detected selective leaching, shall be quantified and evaluated against system and component design requirements. Minimum wall thickness requirements shall be met at all locations of detected selective leaching. In the evaluation of results from volumetric non-destructive and/or destructive examinations, the extent of selective leaching shall be estimated and projected through the end of the operating life. No credit is used for the material properties of the de-alloyed portion of the component during fitness-for-service evaluations.

- Corrective actions:

Engineering evaluations are performed for test or inspection results that do not satisfy established acceptance criteria. Corrective actions are accomplished through the plant’s corrective actions programme to ensure that conditions adverse to quality are promptly corrected. If the deficiency is assessed to be significantly adverse to quality, the cause of the condition is determined and an action plan is developed to preclude repetition. Unacceptable inspection findings result in additional inspection(s) being performed, which may be on a periodic basis, or in component repair or replacement.

- Operating experience feedback and feedback of research and development results:

This AMP addresses the industry-wide generic experience. Relevant plant-specific operating experience is considered in the development of the plant AMP to ensure the AMP is adequate for the plant. The plant implements a feedback process to periodically evaluate plant and industry-wide operating experience and research and development (R&D) results, and, as necessary, either modifies the plant AMP or takes additional actions (e.g., develop a new plant-specific AMP) to ensure the continued effectiveness of the ageing management.

Selective leaching has been detected in components constructed from cast iron, brass, bronze, ductile iron and aluminum bronze (e.g., [5, 7-8, 10, 14]). Affected components have included valve bodies, pump casings, piping, and cast-iron fire protection piping buried in soil. The elements that comprise the inspections (e.g., the scope of the inspections and inspection techniques) are consistent with industry practice and guidance from the appropriate regulatory body.

Appropriate sources of external operating experience are e.g. Owner’s Groups, OECD-NEA, WANO, INPO, IAEA, EPRI and NRC generic communications.

The mechanical hardness in regions of a component damaged by selective leaching is substantially less than for the remaining, undamaged regions of the component.  Hardness testing can generally discriminate between points on the surface of a component affected by selective leaching and those that remain nominal if accurate methods are used.  However, point measurements of the surface hardness of a component are indicative of only the location where the measurement was made and should not be used alone to generalize the state of component health in the surrounding regions.  Additionally, research conducted at EPRI suggests that hardness values indicating the presence of selective leaching should not be used alone to gauge the depth of the selective leaching damage [10, 13].

Nondestructive examination techniques capable of detecting selective leaching have been investigated by EPRI since 2009 [11, 12]. In 2016, an assessment of available NDE methods for selective leaching in cast iron and aluminum bronze materials was published [15]. Best practices and guidance for procedural development to nondestructively detect and characterize selective leaching using ultrasonic methods identified in [15] were further documented and published in 2018 [9]. In 2021, additional test results using ultrasonic techniques to detect and characterize selective leaching degradation in complex shaped gray cast iron valve body components were published [16]. Also in 2021, a variety of electromagnetic NDE techniques were demonstrated to be capable of detecting the presence of selective leaching in gray cast iron piping components [17].

As of 2022, industry research is on-going related to the development of common risk-based approaches to ageing management programme implementation, including demonstration of applying risk-insights to specific ageing management programmes. In 2020 and 2021, an example of applying risk concepts to a selective leaching ageing management programme was investigated [18] which has not been implemented at a NPP. Risk-based approaches to sample populations can assist with targeting inspections to the locations most susceptible to degradation and with highest consequence of failure. Research has also been initiated and planned for follow-up related to metallurgical and environmental factors that affect susceptibility to selective leaching specifically [19].

- Quality management:

In line with SSG-48 [20], Section 4.9 of the IGALL Safety Report [21] gives general information about the expected contents of this attribute in terms of (a) administrative controls, (b) safety analysis report supplements, (c) performance indicators, (d) confirmation (verification) process and (e) data collection and record keeping. Further guidance is available in Paras 3.13.16 – 3.13.17 of SSG-61 [22] on the safety analysis report supplements, in GS-G-3.1 [23] on the confirmation process (paras 6.76 – 6.77 for preventive actions and paras 6.66 – 6.75 for corrective actions), while Section 2 of SRS No. 106 [24] contains good practices on data collection and record keeping for ageing management.

No additional specific information is available for this programme.

References

- FONTANA, M. G., Corrosion Engineering, McGraw Hill, p 86-90, 1986

- SCHWEITZER, P. A., Encyclopedia of Corrosion Technology, 2nd Ed, Marcel Dekker, p 201-202. March 17, 2004

- Age Related Degradation Inspection Method and Demonstration: In Behalf of Calvert Cliffs Nuclear Power Plant License Renewal Application, EPRI, Palo Alto, CA: 1998. TR-107514

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Technical Bases for Changes in the Subsequent License Renewal Guidance Documents NUREG-2191 and NUREG-2192 (NUREG-2221), USNRC, December 2017

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Generic Aging Lessons Learned for Subsequent License Renewal (GALL-SLR) Report — Final Report (NUREG-2191), USNRC, 2017

- UNITED STATES NUCLEAR REGULATORY COMMISSION, 10 CFR Part 50, Appendix B, Quality Assurance Criteria for Nuclear Power Plants, Office of the Federal Register, National Archives and Records Administration, USNRC, Latest Edition

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Information Notice No. 84-71: Graphitic Corrosion of Cast Iron in Salt Water, USNRC, 1984

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Information Notice No. 94-59: Accelerated Dealloying of Cast Aluminum-Bronze Valves Caused by Microbiologically Induced Corrosion, USNRC, 1984

- ELECTRIC POWER RESEARCH INSTITUTE, Nondestructive Evaluation: Guidance for Conducting Ultrasonic Examinations for the Detection of Selective Leaching, EPRI, Palo Alto, CA: 2018.

- ELECTRIC POWER RESEARCH INSTITUTE, Selective Leaching: State-of-the-Art Technical Update. 3002013168 EPRI. Palo Alto, CA: 2019. 3002016057.

- ELECTRIC POWER RESEARCH INSTITUTE, NDE for Selective Leaching of Gray Cast Iron Components. 1018939. EPRI, Palo Alto, CA: 2009.

- ELECTRIC POWER RESEARCH INSTITUTE, Nondestructive Evaluation: Update to NDE for Selective Leaching of Gray Cast Iron Components. 1019111. EPRI, Palo Alto, CA: 2009.

- ELECTRIC POWER RESEARCH INSTITUTE, Nondestructive Evaluation: Correlation of Selectively Leached Thickness to Hardness for Gray Cast Iron and Brass. 1025218. EPRI, Palo Alto, CA: 2012.

- ELECTRIC POWER RESEARCH INSTITUTE, Non-Class 1 Mechanical Implementation Guideline and Mechanical Tools, Revision 4. 1010639.EPRI, Palo Alto, CA: 2006.

- ELECTRIC POWER RESEARCH INSTITUTE, Assessment of Available Nondestructive Evaluation Techniques for Selective Leaching: Technology Review. 3002008013. EPRI, Palo Alto, CA: 2016.

- ELECTRIC POWER RESEARCH INSTITUTE, Ultrasonic NDE Techniques for Detection of Selective Leaching in Complex Shaped Gray Cast Iron Components. 3002020830 EPRI, Palo Alto, CA: 2021.

- ELECTRIC POWER RESEARCH INSTITUTE, Electromagnetic NDE Techniques for Detection of Selective Leaching in Gray Cast Iron Piping. 3002020832.EPRI, Palo Alto, CA: 2021.

- ELECTRIC POWER RESEARCH INSTITUTE, Long-Term Operations: Leveraging Risk Insights for Aging Management Program Implementation. 3002018403. EPRI, Palo Alto, CA: 2020.

- ELECTRIC POWER RESEARCH INSTITUTE, Accelerated Testing and Evaluation of Factors Affecting Selective Leaching Susceptibility. 3002020822. EPRI, Palo Alto, CA: 2021.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management and Development of a Programme for Long Term Operation of Nuclear Power Plants, Specific Safety Guide, Safety Standards Series No. SSG-48, IAEA, Vienna (2018).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management for Nuclear Power Plants: International Generic Ageing Lessons Learned (IGALL), Safety Reports Series No. 82 (Rev. 2), IAEA, Vienna. Preprint.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Format and Content of the Safety Analysis Report for Nuclear Power Plants, SSG-61, IAEA, Vienna (2021).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Application of the Management System for Facilities and Activities, GS-G-3.1, IAEA, Vienna (2006).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Ageing Management and Long Term Operation of Nuclear Power Plants: Data Management, Scope Setting, Plant Programs and Documentation, Safety Report Series No. 106, IAEA, Vienna (2022)